## Assesment
Assesment of heat demand covering transmision and infiltration losses | [8 empty] | Minimum demands from building code
Floor space | 17000 | m2 | Hygienic minimum ventilation rate, building | 0 | m3/h/m2 | Maximum air leakage from building codes |  | 1.5 | U floor | 0.1 | W/m2K
Occupance design | 850 |  | Hygienic minimum ventilation rate, people | 21.6 | m3/h/pers |  |  |  | U window | 0.8 | W/m2K
|  |  | Total hygienic minimum ventilation rate | 1.08 | m3/h/m2 |  |  |  | U wall | 0.18 | W/m2K
T soil. Set to annual mean temperature | 12 | °C | Actual minimum ventilation rate (1.2) | 1.3 | m3/h/m2 |  |  |  | U roof | 0.13 | W/m2K
T Indoor | 22 | °C | Efficiency recuperator in AHU | 80% |  | Air change due to infiltration | 0.105 | per hour | leakage number at 50 Pa | 1.5 | per hour
Design Ambient temperature | -1.9 | °C | ΔT supply air / room temperature | 0 | K |  |  |  | Recuperatorefficiency | 80%
|  |  | ΔT supply air from fan power | 0 | K
Length of the building | 125 | m | Transmision |  |  | Infiltration |  |  | Ventilation
Width | 17 | m | U floor | 0.1 | W/m2K | Volume of the building | 51000 | m3 | Total air flow | 22100 | m3/h
Number of storages | 8 | stk | U window | 0.8 | W/m2K | Air change | 0.105 | per hour | Supply air temperature | 22 | C
Storage hight | 3 | m | U wall | 0.18 | W/m2K | Air flow | 5355 | m3/h
Window share of building envelope | 30% |  | U roof | 0.13 | W/m2K |  |  |  | Supply air temperature after recuperator | 17.22 | C
Incline roof | 12 | ° | Heat loss floor | 2125 | W |  |  |  | Supply air temperature after heating coil | 22 | C
Roof width | 17.3798 | m | [6 empty] | ΔT heating coil | 4.78 | K
|  |  | Heat loss windows | 39096.576 | W
Area floor to ground (footprint) | 2125 | m2 | Heat loss walls | 20657.8358 | W |  |  |  | Heat demand heating coil | 35740.8567 | W
Area building fasades | 6816 | m2 | Heat loss roof | 6749.876 | W
Area windows | 2044.8 | m2
Wall area from gable/roof incline | 30.7144 | m2 | Total transmision heat loss | 68629.2878 | W | Q infiltrasjon | 43301.4225 | W | Heat demand from subtemperature suplly air | 0 | W
Area wall | 4801.9144 | m2
Area roof | 2172.4738 | m2 | Q trans og inf. | 111930.7103 | W
|  |  | Q tot, design building heating | 111930.7103 | W
|  |  | Q tot, design, heating system | 147671.567 | W | 147.7 | kW
|  |  | q trans&inf | 6.5842 | W/m2
|  |  | q vent | 2.1024 | W/m2
|  |  | q tot des | 8.6866 | W/m2

## Building code demands
|  | Roof | Floor | Outer walls | Windows | Air leakage | Recuperator efficiency
| TEK97 | 0.15 | 0.15 | 0.22 | 1.6 | 4 | 60% | 1
| TEK07 | 0.13 | 0.15 | 0.18 | 1.2 | 3 | 70% | 2
| TEK10 | 0.13 | 0.15 | 0.18 | 1.2 | 1.5 | 70% | 3
| TEK17 | 0.13 | 0.1 | 0.18 | 0.8 | 1.5 | 80% | 4
| Low energy building | 0.1 | 0.1 | 0.15 | 0.8 | 1 | 80% | 5
| Passiv house | 0.08 | 0.08 | 0.1 | 0.8 | 1 | 80% | 6
4 | TEK17 | 0.13 | 0.1 | 0.18 | 0.8 | 1.5 | 80%